## Slide 1
Fast-tripping Protection Schemes for DC Microgrids
Ali Bidram
University of New Mexico
January 21, 2022

## Slide 2: Power and Energy Program at UNM
A multidisciplinary research program working on multiple aspects of society's energy needs and networked systems:
power system control and protection,
microgrid and smart grid design and operation,
integration of distributed energy resources, Power Electronics, Storage and Electric Vehicles,
novel photovoltaics (PV) materials for better solar cells.

## Slide 3: UNM Microgrid
  PV system (50kW)
  Lead-acid battery energy storage system (50kW/90kWh)
  Natural Gas generator (240kW)
  Fuel Cell (80kW)
  hot and cold thermal storage, and an absorption chiller.

## Slide 4: PSET Laboratory
Power Systems Emerging Technologies (PSET) lab:
Power and Control Hardware-in-the-Loop (HIL) Testbed

## Slide 5: Introduction to smartgrids
Smartgrid refers to a class of technology that modernizes utility electricity delivery systems using computer-based remote control and automation.
Reliability
Sustainability
Efficiency

## Slide 6: What is a microgrid?
Microgrid, as the main building block of smartgrids, is a group of interconnected loads and distributed energy resources.
Microgrid has the ability to
work in both grid-connected
and islanded modes.
Photo from: http://www.horizonenergygroup.com
Department of Energy:
Microgrid applications:
Rural plants.
Business buildings, hospitals,
and factories
Forward operating bases
AC Microgrids
DC Microgrids:
  DC microgrids render increased efficiency compared to their AC counterparts and flexibility for the integration of DC power sources (e.g., photovoltaic and battery energy storage systems).
Microgrid types:

## Slide 7: Power System Protection
Power system protection’s task is to detect and isolates faults (short circuits) in the system.

## Slide 8: Protection Challenges in DC Microgrids
DC systems fault signature
  The signature of dc fault currents is their very high magnitude with the peak usually attained within a couple of milliseconds after the onset of a fault:
    Can damage IGBT switches in converters
    IGBTs are blocked when the current is largely above their thermal inertia
    Blocked IGBT  Losing controllability over the converter

## Slide 9: Travelling Waves
TWs are electromagnetic waves propagated along the power system equipment such as lines or cables when a disturbance (e.g., fault, lightning, switching, etc.) occurs

## Slide 10: Multiresolution Analysis
In order to effectively construct wavelets over a wide frequency range, multiresolution analysis (MRA) is a practical approach for fully implementing the DWT.
Once the MRA based wavelet coefficients are identified, the Parseval’s theorem is used to calculate the energy corresponding to the identified coefficients

## Slide 11: High-Frequency Fault Signatures in a DC system

## Slide 12: High-Frequency Fault Signatures in a DC system
1 MHz Sampling Frequency
2 MHz Sampling Frequency

## Slide 13: Pole to Ground Faults

## Slide 14: Pole to Pole Faults
Impact of PP fault on pole to pole and pole to ground voltages’ Parseval energy

## Slide 15: Fault Detection and Location Algorithm
Fault detection and location algorithm
Fault classification using SVM
Fault location using Gaussian Process

## Slide 16: Verification Results
Verification results
Cable | Bolted PP | Resistive PP | Bolted PG | Resistive PG
C1 | 4.9% | 3.6% | 2.5% | 4.1%
C2 | 5.1% | 2.9% | 3.9% | 1.1%
C3 | 4.7% | 6.1% | 4% | 2.7%
C4 | 1.1% | 0.4% | 2.1% | 0.2%
C5 | 6.3% | 0.6% | 0.8% | 0.6%
C6 | 5.3% | 4.8% | 6.2% | 3.4%
Fault Location Estimation Error
C4 bolted PP faults
C4 resistive PP faults
C4 bolted PG faults
C4 resistive PG faults